## Slide 1: ELI Beamlines Overview of a control system of a high-power laser facility
Karel Majer
DEELS ’22, Berlin, 07/06/22

## Slide 2: ELI (Extreme Light Infrastructure)
World's largest and most advanced high-power laser infrastructure and a global technology and innovation leader in high-power, high-intensity, and short-pulsed laser systems.
First ESFRI Landmark constructed in the Central Eastern European Member States. Three world-class high-power, high-repetition-rate laser facilities have been established in Czech Republic (ELI Beamlines), Hungary (ELI-ALPS) and Romania (ELI-NP).
The commissioning of the facilities is foreseen to be completed in 2022-2023.

## Slide 3: ELI facilities
ELI Beamlines (Prague, CZ)
4 high-power fs laser systems
Particle acceleration, X-ray generation, plasma science
ELI-ALPS (Szeged, HU)
Ultra-short pulses from THz to X-rays
Attosecond science (electron processes, chemical reactions)
ELI-NP (Magurele, RO)
2x10 PW laser
Gamma beam source (to 19 MeV)
Nuclear physics

## Slide 4: ELI Beamlines facility

## Slide 5: ELI Beamlines lasers
Beamline | L1 | L2 | L3 | L4
Peak power | 5 TW | 100 TW | 1 PW | 10 PW
Pulse energy | 100 mJ | 2 J | 30 J | 1,5 kJ
Pulse length | 20 fs | 15 fs | 30 fs | 150 fs
Re. rate | 1 kHz | 50 Hz | 10 Hz | 0,1 Hz
Developer | ELI Team | ELI Team + Rutherford Appleton Laboratory | Lawrence Livermore National Laboratory + ELI Team | National Energetics + Ekspla + ELI Team
Technology | Diode pumping, OPCPA | Diode pumping, OPCPA | Square beam 214 mm x 214 mm, Ti:Sapphire amps and diode and Nd:glass pump lasers | Square beam 625 mm x 625 mm, Discharge lamp pumped Nd:glass amps + OPCPA pre-amps

## Slide 6: Mode locking

## Slide 7: Chirped pulse amplification

## Slide 8: L4 compressor chamber

## Slide 9: ELI Beamlines experiments
Laser as X-ray source:
Laser beam -> plasma -> electrons accelerated by EM field -> X-ray beam
Bio/molecular research
Plasma physics
Particle acceleration
X-ray sources
Exotic physics
ELIMAIA – ion acceleration

## Slide 10: ELI Beamlines laser control system

## Slide 11: Software architecture
Mostly programmed in LabVIEW – many parallel processes on each controller
LabVIEW-native EPICS implementation (Obsevatory Sciences, modified by ELI)
Easy setup of PVs in MySQL configuration database
LabVIEW framework for creating EPICS-based GUIs
Device monitoring & EPICS
Cameras
Environment monitor
3x pointing

## Slide 12: Safety systems
Personnel safety
Pilz PLCs (SIL rating)
Controls when laser may be turned on and propagated
State machine paradigm for each area
  No emission
  Low power
  High power
Radiation confined to experimental halls, separate monitoring system (contractor)
Vacuum control
NI RIO (with FPGA) or B&R PLCs
Big volumes, separate roughing and forevacuum primary pumps
Abstraction to a set of state machines
Machine safety
Pilz or B&R PLCs
Guarantees valid laser beampath
Beamline divided into zones
  No emission, low power, high power

## Slide 13: Common system description
We can abstract many systems to a set of Mealy state machines:
Personnel safety (6)
Machine safety (7)
Vacuum control (10+)
Pneumatics control (2)
Environment monitors
Fast interlock for 1 kHz laser
Unified description format for all of them
Systems fully described in Excel spreadsheets

## Slide 14: Description in a spreadsheet
IO declaration

## Slide 15: Description in a spreadsheet
Transition matrix

## Slide 16: Description in a spreadsheet
Triggers & permissions

## Slide 17: Description in a spreadsheet
Outputs

## Slide 18: Code generators
Full description in spreadsheet – can we program systems only by changes in Excel?
Yes, we can! (although some people don’t believe that)
LabVIEW parser to extract data from Excel to LabVIEW dictionary or JSON
System description passed to scripters developed for each application type
Unified simulation and diagnostics tools

## Slide 19: Code generators
Pilz scripter
Generates “hardcoded” ST code
PAS4000 API used to create ready-to-build project
Verified for safety-rated applications
LabVIEW FPGA scripter
FPGA runs spreadsheet interpreter
System description stored in RAMs
Generated RAM and IO definitions
Configuration changes – only RAM contents -> no recompilation
B&R scipter
Generates XML files to create ready-to-build project
Partially “hardcoded” ST code
Dynamic version under development

## Slide 20: Timing system
GPS – timestamp + 1 pulse per second
Rb clock as GPS receiver
-> 1 PPS, 10 MHz, NTP timestamp to White Rabbit grandmaster
White Rabbit distributed through facility to synchronize all lasers and experiments
Timestamping not too difficult, we know when an event (shot) occurs, highest rep rate 1 kHz

## Slide 21: Timing system
Seed laser – usually 80 MHz Ti:Sapphire optical oscillator
RF oscillator + feedback loop to compensate for frequency drift in optical cavity
ETS generates 1 kHz trigger signals -> pulse picking in Pockels cells -> 1 kHz laser
1 kHz trigger distributed through beamline

## Slide 22: Data presentation
LCS team gather data, but do not operate lasers nor run experiments
Direct access to controls confined to integration layers – only in control rooms
Operators require data even in offices or remotely

## Slide 23: Thank you
Karel Majer
karel.majer@eli-beams.eu
Acknowledgement: Birgit Plötzeneder, Jack Alexander Naylon